Design and Economic Analysis of a Geothermal Vertical Coupled Heat Pump System for the University of Tennessee Campus

Joey Birchfield

Jason Cho

Will Kester

Table of Contents

- Introduction

- Synthesis Information for Processes

- Method of Approach

- Results

- Capital Cost Estimates

- Discussion of Results

- Conclusions

- Recommendations

- References

- Appendices

- Introduction

The purpose of this report is to document a study-level design and economic analysis of a vertical ground coupled heat system (VGCHPS) for the University of Tennessee campus. Commercial geothermal heat pump systems are being developed to provide clean energy and reduce overall heating and cooling costs. VGCHP’s are closed loop system’s which use a reversible vapor compression cycle linked to an underground heat exchanger. Both the water to air and the water to water heat pumps utilize a circulating water-antifreeze solution. The solution circulates through an underground piping network and through a liquid-to-refrigerant coil. Fluid to be heated or cooled is circulated through a fluid-to-refrigerant coil and is transported to the point of utilization. VGCHPS’s are normally constructed using two polyethylene tubes in the borehole.  The polyethylene tubes are connected at bottom of the bore resulting in a closed U-tube shape. Vertical tube sizes are usually in the range from ¾ to 1.5 inches nominal diameter. Depending on drilling conditions and underground soil properties the vertical bore depths can range from 50 to 600 feet deep.

The design objectives of this project are (1) develop a flow sheet for the design process of the VGCHP system, (2) present relevant material and energy balances, (3) provide estimates of the initial capital cost and determine the payback period, and (4) compare the estimated economics of the VGCHPS with the current heating and cooling costs for the University of Tennessee.The heating requirements on campus are met by a central steam plant that uses three coal fired boilers capable of burning a total of 300,000 pounds of coal per hour and a natural gas fired turbine generator rated at 5 MW. The cooling requirements are met by a combination of 3,000 window air conditioners ranging from 5,000 to 32,000 BTU, 500 split and package systems ranging from 1 to 60 tons, and 92 chillers ranging from 20 to 995 tons. The total cooling capacity available from all the air conditioning equipment is approximately 30,000 tons. The University of Tennessee Facilities Services has requested the study level design of a geothermal HVAC system capable of replacing 3 chillers that provide 2400 tons cooling energy for the agriculture portion of campus. The 2400 tons of cooling was reduced to 600 tons due to limited space on the Agricultural Campus. This design is focused on delivering 600 tons of cooling.

This project is supported by Facility Services at the University of Tennessee (UT).  This report documents a study-level design and economic analysis of the procurement and installation of a ground-source heat pump at UT and was prepared in Spring Semester, 2014 as fulfillment of course requirements of CBE 488 (Sustainable Design Internship) at the University of Tennessee.  Advisors for this project are D. W. Bailey and T.E. Ledford of UT Facility Services and J.S. Watson and R. M. Counce of UT Chemical and Biomolecular Engineering Department.

2.0 Synthesis Information for Processes

2.1 Input Information

To determine the input information for this design we used several resources including the Engineering Group Design1, Kavanaugh and Rafferty’s Design Guide2. The requested amount of cooling to replace was 2400 tons but upon the completion of calculations, it was deemed impossible to replace 2400 tons with the green space available for the bore field. To determine the maximum cooling load that could be replaced, we utilized the largest open area and back calculated to determine the load that the area could withstand. The largest space on the Agricultural Campus was able to replace a total of 600 tons of cooling. Due to the size limits of the spreadsheet, the borehole field was divided into three equal parts each having a total cooling load of 200 tons and the hourly, monthly, and yearly ground loads were calculated using this number and the Design Guide2.

In 2009, Engineering Services Group INC and Mid-State Construction completed an engineering study to determine the economic feasibility of using a VGSHP at the future University of Tennessee Sorority Village1. From this report we were able to get ground property information including thermal conductivity, thermal diffusivity, and local ground temperature. To verify that the information provided in the Engineering Services Group study we compared their values with values reported by the Tennessee Valley Authority from their geothermal test well data3.

We were also able to obtain recommended values for design variables such as the equivalent diameter of the bore and the spacing between adjacent bores. Much of the physical property data and input information was determined using the Kavanaugh and Rafferty Geothermal Design Guide2.

The remaining borehole specifications were calculated based on the properties of the one and a quarter inch high density polyethylene pipe. To determine the type of grout to use and the grout properties, GeoPro Inc., who specializes in geothermal grouts, was contacted and provided a recommended type of grout along with its properties.

Figure 2.1 shows the hierarchal structure of the spreadsheet that will be used to calculate the depth of each borehole. For a single borehole, the user must input the heating or cooling loads generated by the building, soil properties, heating or cooling fluid properties, heat pump outlet temperature, average fluid temperature in the borehole, and the characteristics of the borehole, such as the radius of the borehole. For a borefield, all of the information required for a single borehole is included as well as the distance between boreholes, number of boreholes, and the aspect ratio of the borefield.

Figure 2.1: Flow for Design

Table 2.1: Ground Loads

| peak hourly ground load | qh | W | 703370 |
| --- | --- | --- | --- |
| monthly ground load | qm | W | 179316 |
| yearly average ground load | qy | W | 3160 |

The inside of the borehole must have enough area for spacing of both pipes as well as the grout. The optimal spacing to reduce thermal effects is to have an equal distance between the wall and each pipe as well as between the pipes4. This leads to a center-to-center distance of 0.0541 m.

Table 2.2: Borehole Characteristics

| borehole radius | rbore | m | 0.06 |
| --- | --- | --- | --- |
| pipe inner radius | rpin | m | 0.0173 |
| pipe outer radius | rpext | m | 0.0211 |
| grout thermal conductivity | kgrout | W.m-1.K-1 | 2.076 |
| pipe thermal conductivity | kpipe | W.m-1.K-1 | 0.133 |
| center-to-center distance between pipes | LU | m | 0.0541 |
| internal convection coefficient | hconv | W.m-2.K-1 | 1000 |

Figure 2.2: Borehole Characteristics

2.2 Physical Properties

Table 2.3: Ground Properties

| thermal conductivity | k | W.m-1K-1 | 1.4358 |
| --- | --- | --- | --- |
| thermal diffusivity | α | m2.day-1 | 0.151 |
| Undisturbed ground temperature | Tg | °C | 14.44 |

Coolant Fluids

Heating and cooling fluids used in geothermal applications differ from the typical heating and cooling fluids used in commercial settings. The main reason for the difference is the risk of ground water contamination. Taking into account the possibility for contamination, the fluids that are recommended to be used for vertical closed loop geothermal applications are as follows: food-grade propylene glycol-water solution, methanol-water solution of up to 20 percent methanol by volume, ethanol-water solution of up to 20 percent ethanol by volume5. The selection of the coolant fluid relies heavily on the amount of heat transfer necessary. We have chosen 50% propylene glycol as our cooling liquid because it best meets the requirements for the cooling.

Table 2.4: Fluid Properties

| thermal heat capacity | Cp | J.kg-1.K-1 | 3558.78 |
| --- | --- | --- | --- |
| total mass flow rate per kW of peak hourly ground load | mfls | kg.s-1.kW-1 | 0.148 |
| max/min heat pump inlet temperature | TinHP | °C | 4.44 |

2.3 Software Parameters

The calculations for the sizing of the borehole depth are carried out in a spreadsheet.The spreadsheet was compared against more advanced software tools and proved to be accurate with the other software tools’ results4. These calculations require a specific set of inputs that must be within certain ranges for the spreadsheet to yield accurate results. These inputs and ranges are as follows:

0.05 m ≤ rbore ≤ 0.1 m

0.025m2/day≤α≤ 0.2m2/day

-2 ≤ln(t/ts) ≤ 3

4 ≤ NB ≤ 144

1 ≤A≤ 9

rbore is the radius of the borehole

α is the ground thermal diffusivity

t is the ground load

ts is the characteristic time

NB is the number of boreholes

A is the geometrical aspect ratio

3.0 Method of Approach

The first step in designing a VGCHP capable of heating or cooling a portion of the UT agricultural campus was to research similar commercial applications. Information on other similar scale geothermal applications was published in the literature by Ball State University and The University of North Dakota6.

Software produced by ASHRAE has a high level of accuracy when compared with other design calculations. Vertical closed loop geothermal design software created by Michael Philippe et al will be used in our design calculations4. In using the software, we will fill in all of the input parameters and allow the software to calculate the borefield size and depth of bores.

The next step in our method of approach is to find a space on campus large enough to support the bore field size determined by the heating and cooling loads. Next, we will calculate the raw material costs, installation costs, and operating costs.

After computing all the cost information, we will compare our cost estimates with a spreadsheet compiled by Steve Kavanaugh7 that contains all the cost information for approximately fifty commercial geothermal heating and cooling systems. Provided our numbers are similar when compared to other installed geothermal HVAC systems of similar size, we will make a recommendation between the current University heating and cooling methods or investing in a geothermal cooling system. We will also take into account the payback period of the project and factors including public perception of sustainable energy and impact on parking for the Agricultural Campus.

4.0 Results

Borefield Sizing

In order to determine if we could design a geothermal HVAC system capable of replacing 2400 tons of cooling capacity, it was necessary to determine the amount of land available on the agricultural campus where the borefield could be placed. Using Google Earth’s satellite imagery we were able to examine all the open space on campus where the borefield could be installed. The only space that was able to provide adequate area for the borefield was a large staff parking lot located on the agricultural campus between the greenhouses and the College of Veterinary Medicine. The parking lot was measured as 240 meters long and 65 meters wide and this area provides sufficient space to install a borefield capable of meeting a portion of the requirements specified by Facilities Services (600 tons of cooling capacity).

Figure 4.1: Location of Borefield

4.1 First Set of Results

The first set of results calculated by the ASHRAE software can be seen in Tables 4.1, 4.2, and 4.3. These values include resistances of the boreholes, piping, as well as the effective ground thermal resistances over different time periods. The first set of results also includes an initial calculation of the heat pump outlet temperature, average fluid temperature in the borehole, and the total length of drilling for all of the bores. After the software calculates these values a new set of inputs must be entered for iteration to come up with an optimized solution. The new set of inputs can be seen in table 2.8 and include the distance between bores, number of boreholes, and the borefield aspect ratio. The borefield aspect ratio is the number of bores in the longest direction divided by the number of bores in the shortest direction. Given that we are working with a set distance between bores and a set area from the parking lot, there was only one optimal aspect ratio we could use to make sure the borefield fit in our given area.

Table 4.1: Effective Borehole Resistance

| convective resistance | Rconv | m.K.W-1 | 0.004 |
| --- | --- | --- | --- |
| pipe resistance | Rp | m.K.W-1 | 0.201 |
| grout resistance | Rg | m.K.W-1 | 0.020 |
| effective borehole thermal resistance | Rb | m.K.W-1 | 0.122 |

Table 4.2: Effective Ground Thermal Resistances

| short term (6 hours pulse) | R6h | m.K.W-1 | 0.163 |
| --- | --- | --- | --- |
| medium term (1 month pulse) | R1m | m.K.W-1 | 0.252 |
| long term (10 years pulse) | R10y | m.K.W-1 | 0.266 |

Table 4.3: Total Length of Bore

| heat pump outlet temperature | ToutHP | °C | 2.5 |
| --- | --- | --- | --- |
| average fluid temperature in the borehole | Tm | °C | 3.5 |
| total length | L | m | 5626.4 |

Table 4.4: Borefield Characteristics (2nd Inputs)

| distance between boreholes | B | m | 6.1 |
| --- | --- | --- | --- |
| number of boreholes | NB | - | 117 |
| borefield aspect ratio | A | - | 1.44 |

4.2 Second Set of Results

After the second set of inputs is entered into the software and iterative procedure is performed to achieve a final set of results. The results include the total borefield length, the depth per bore, and a temperature penalty. The temperature penalty arises when heat transfer in the ground is inadequate and the borefield begins to change the temperature of the ground.

Table 4.5: Iterative Software Results

| distance-depth ratio | B/H | - | 0.044 |
| --- | --- | --- | --- |
| logarithm of dimensionless time | ln(t10y/ts) | - | -1.359 |
| temperature penalty | Tp | °C | -0.204 |
| total borefield length | L | m | 16436.7 |
| 2nd iteration |  |  |  |
| distance-depth ratio | B/H | - | 0.043 |
| logarithm of dimensionless time | ln(t10y/ts) | - | -1.396 |
| temperature penalty | Tp | °C | -.199 |
| total borefield length | L | m | 16430 |
| 3rd iteration |  |  |  |
| distance-depth ratio | B/H | - | 0.043 |
| logarithm of dimensionless time | ln(t10y/ts) | - | -1.395 |
| temperature penalty | Tp | °C | -0.199 |
| total borefield length | L | m | 16430.2 |
| 4th iteration |  |  |  |
| distance-depth ratio | B/H | - | 0.043 |
| logarithm of dimensionless time | ln(t10y/ts) | - | -1.396 |
| temperature penalty | Tp | °C | -0.199 |
| total borefield length | L | m | 16430.2 |
| 5th iteration |  |  |  |
| distance-depth ratio | B/H | - | 0.043 |
| logarithm of dimensionless time | ln(t10y/ts) | - | -1.396 |
| temperature penalty | Tp | °C | -0.199 |
| total borefield length | L | m | 16430.2 |
| Final results |  |  |  |
| total borefield length | L | m | 16430.2 |
| borehole depth | H | m | 140.4 |

4.3 Geothermal Ground Source Heat Pump

The heat pumps chosen for this design are manufactured by Daikin and the model is the WLVW1290 24 ton unit. For pricing and information on which heat pump would best suit our needs we contacted Daikin. Duke Hoffman, a representative from Daikin, was able to provide us with a cost estimate for the best model that would suit our application and the models exact specifications. The specifications and order for the cost estimate can be seen in Table 4.6 and the Appendices.

The WLVW 1290 is designed specifically for vertical geothermal applications and can be applied to all building types. The heat pump is constructed of G-60 galvanized steel and is insulated with dual density fiberglass. This heat pump also comes equipped with a thermal expansion valve for refrigerant metering. This allows the unit to operate at optimum efficiency with fluid temperatures ranging from 25 to 100 degrees Fahrenheit. A MicroTech III Unit Controller coupled with a BACnet communication module allows for multiple heat pumps to be controlled simultaneously using network communications8. The exact specifications for the heat pump operation can be seen in Table 4.6.

The most important factors regarding the performance of the heat pump are the coefficient of performance (COP) and the energy efficiency ratio (EER)9. The COP is the ratio of heating or cooling provided to the electrical energy consumed. The COP is dependent on the operating conditions, and a higher COP will lead to lower operating costs. The EER is a ratio of output cooling energy to the electrical input energy. The EER measures the efficiency of a cooling system operating at steady state over a specific duration of time. The EER and COP will be used as a tool to compare costs of a conventional HVAC system against the geothermal design.

Table 4.6: Heat Pump Performance and Specifications7

Figure 4.2: Heat Pump Performance

4.4 Borefield Layout

In Figure 4.3 you can see the design and layout of the geothermal borefield. The field is divided into 3-200 ton capacity sections and the circulating fluid can be routed to the heat pumps located in the surrounding buildings. When calculating the amount of piping needed, an extra length of 1000 feet per field was added to transport the heating/cooling fluid to the heat pumps. In between each field section there are two separate pipes to carry the hot and cold fluid which are represented by the red and blue lines.

Figure 4.3: Borefield Layout

5.0 Capital Cost Estimates

The raw material costs and installation costs cited in the study level design were obtained using sources on the web and the Geothermal Design guide. The ground loop installation cost per foot is recommended by Kavanaugh and Rafferty and can fall in the range of five dollars to eight dollars per foot. This price includes labor costs, U-tube insertion, backfilling, and header installation at 4 feet and assumes bentonite grout to forty feet of a 500 foot average bore depth, header to equipment room distance in 150 feet and the surface casing is less than 40 feet. It also states the cost can be near upper range or exceeded if the contractor has a high travel cost, the entire bore must be grouted, cuttings must be disposed off site, labor rates are higher than average, or nonstandard header arrangements are specified.

We also checked various website for pricing information on the HDPE piping and propylene glycol solution and all sources had approximately equal prices. The pricing for the connectors, tees, u bends, and elbows was obtained from HDPE Supply10. To determine the amount of bentonite grout and pricing information we contacted the GeoPro Inc. Company. The representative from their company recommended the best grout for our application and also gave us a price per bag. Their website has a tool that allows you to input your design parameters and calculates the amount of bentonite grout needed to backfill the bores. Using this tool we were able to calculate the number of bags of bentonite needed11. The propylene glycol solution was priced per gallon from ChemWorld’s website12.

Table 5.1: Material Costs for 200 tons

| Material | Cost Per Unit | Total number of Units | Total Cost |
| --- | --- | --- | --- |
| 1.25 in HDPE Pipe | $0.48 per foot | 19,270 feet | $9,250 |
| HDPE Connetors | $2.22 per 20ft | 964 | $2,140 |
| U bend connectors | $11.50 | 117 | $1345.50 |
| Elbows | $5.93 | 234 | $1387.62 |
| Tee’s | $7.19 | 117 | $841.23 |
| 99.9% Propylene Glycol | $18.18 per gallon | 180 gallons | $3272.4 |
| TG Thermal Grout | $8.25 per bag | 2,766 Bags | $22,819.5 |
| Daikin WLVW1290 24 ton | $13,600 | 9 units | $122,400 |

Table 5.2: Labor and Construction Costs for 200 tons

| Job | Cost Per Unit | Total Number of Units | Total Cost |
| --- | --- | --- | --- |
| Ground Loop Installation | $6.50 | 53,820 | $353,080 |
| Drilling Cost | $15 per foot | 53,820 feet | $807,300 |

Table 5.3 Total Capital Cost Summary for 600 Tons Cooling

| Material/Job | Total Units | Total Cost |
| --- | --- | --- |
| Piping (HDPE, Connectors, elbows, tees) | 1055 connectors, 351 U-bends, 702 elbows, 351 Tees | $204,944 |
| Circulating fluid | 540 gallons | $9,817 |
| Grouting | 8,298 bags | $68,458 |
| Heat Pumps | 25 heat pumps | $340,000 |
| Loop Installation (labor, backfill, pipe fusion, trenching) | 161,460 feet | $1,052,740 |
| Drilling | 161,460 feet | $2,421,900 |
| Total Cost | - | $4,088,000 |

Table 5.4 Inflation and interest rates for different economic conditions

Table 5.5 Initial cost for conventional HVAC and geothermal systems

Table 5.6 Energy load and efficiencies for conventional HVAC and geothermal

Table 5.7 Maintenance cost for conventional HVAC and geothermal

Figure 5.1 Cumulative costs for both the conventional HVAC and geothermal systems

Figure 5.2 Cumulative costs with high natural gas prices

Figure 5.3 Payback Period

6.0 Discussion of Results and Economic Analysis

Due to the size restrictions of the available land, the overall cooling load that is attainable is 600 tons. This value is significantly less than that which is being utilized for the current cooling loads on the Agricultural Campus. A major benefit of this system is that it will not only be able to provide cooling energy in the warmer months, but it will also be able to generate approximately 780,000kwh/yr of energy for heating purposes. The combined ability to heat and cool, operate at a high efficiency, and produce clean sustainable energy are all very important benefits that would be attained by the installation of this system.

All the calculated parameters of the borefield are consistent with typical vertical closed loop geothermal systems. A brief design summary of the system can be seen in Table 7.1. The overall costs associated with the designed system are comparable to systems of similar size that are currently operating7. This means that the cost calculations were accurate and provide a good basis for long term analysis. The operating costs were estimated using several case studies of similar geothermal systems7. Vertical geothermal HVAC systems have very low operating and maintenance costs due to their simple design and few moving parts. The only significant operating costs occur from the electricity required to pump the circulating fluid and the labor to occasionally monitor the system and make sure everything is working properly. The main maintenance cost stems from leaks in the HDPE pipe resulting from age and normal wear. These leaks can be somewhat expensive to repair because of the labor involved in removing the pipe from the bore, repairing the leak, and freshly backfilling the bore.

For economic analysis and to give a comparison between the cumulative costs of a conventional HVAC system versus the geothermal system, three different cases were presented. These cases compared the two systems under strong, nominal, and poor economic conditions. The interest and inflation rates for each economic condition can be seen in Table 5.4. When making this comparison the main components of each system were given a 20 year lifetime. Regardless of the economic conditions, the geothermal system had a much higher cumulative cost compared the conventional HVAC system. We also made one more comparison of the two systems under the assumption of high natural gas prices. Natural gas is currently used as the main source of heating buildings so if the price of natural gas were to dramatically increase this would have a significant impact on the feasibility of a geothermal installation. After about 25 years under a high natural gas price scenario, the geothermal system becomes less expensive than the conventional system. The results of the comparison can be seen in Figure 5.2. More in depth tables with all of the values for the comparisons can be seen in the Appendices in tables 11.1 through 11.9. After determining a total capital cost of about 4 million dollars, the payback period was computed. This system gives a return of investment by reducing heating and cooling costs in the range of 40 to 60 percent. With approximate savings at 50% the payback period under a strong economy would come after about twenty five years and could be as long as thirty years in a poor economy. The results of the payback period calculation can be seen in figure 5.3 and the yearly data can be seen in Appendices tables 11.10 through 11.12.

Table 6.1 Design Summary Table

| Total Length of Borefield | 787 feet |
| --- | --- |
| Total Width of Borefield | 213 feet |
| Total Number of Boreholes | 351 |
| Borehole to Borehole Distance | 20.01 feet |
| Borehole Radius | 0.197 feet |
| Borehole Depth | 460.63 feet |
| Total Borefield Capacity | 600 tons |
| Capital Cost | 4.1 million |

7.0 Conclusions

Currently, it is not economically feasible to install the designed geothermal system. The payback period of a feasible capital cost project of this magnitude is between ten to twenty years. The system that was designed has a payback period of between twenty-five to thirty years. Due to limited space, the already existing conventional HVAC infrastructure, and the high capital cost associated with the geothermal system it is a better economic decision to stick with conventional heating and cooling methods. It would be much more feasible to install a geothermal system if it was under new construction. If natural gas and electricity prices were to significantly increase, then it would justify retrofitting the existing heating and cooling system to include a geothermal system. With natural gas prices currently low the trend only slightly increasing in the future, natural gas appears to be the most economical source of energy for the foreseeable future. The projections for the price of natural gas can be seen in Figure 8.1. Although natural gas may be the best source of energy under current conditions, the fact still remains that natural gas is a non-renewable resource and is not sustainable. With the idea of climate change occurring due to our strong reliance on fossil fuels there may become many new incentives for sustainable energy production in the near future. With new incentives to reduce our carbon footprint and invest in sustainable technology the installation of this geothermal application may become much more feasible in the very near future.

Figure 7.1 Natural Gas Projected Cost16

8.0 Recommendations

It is our recommendation based on the calculated capital costs and payback period that the system not be installed. If sustainability and public perception of sustainability of the University is of great importance, it would be our recommendation to install one of the three loops. Not only would this allow us to give the geothermal application a good “test,” but it would also decrease the overall capital cost of the project while giving notoriety to the University for increasing the presence of sustainable energy on campus. Due to the major scale of construction and limited parking on the Agricultural Campus, it would be our recommendation that only one loop at a time be installed. This would allow two-thirds of the parking lot to remain in use while construction of the boreholes and piping is being installed. This also allows for future loops to be completed with limited parking interference if gas and electricity prices rise and the University decided to increase its sustainable energy.

9.0 References

1Engineering Services Group design of a ground source heat pump system for the UT sorority village

2Kavanaugh, Stephen P., and Kevin D. Rafferty.Ground-source Heat Pumps: Design of Geothermal Systems for Commercial and Institutional Buildings. Atlanta: American Society of Heating, Refrigerating and Air-Conditioning Engineers, 1997. Print. (Design Information)

-3http://www.tva.gov/commercial/TCStudy/ (Property Information)

4Phillippe, Mikael, Michel Bernier, and Dominique Marchio. Vertical Geothermal Bore fields: Sizing Calculation Spreadsheet. N.p.: ASHRAE Journal, 2010. Web. 11 Oct. 2012.  (Software)

5http://www.michigan.gov/documents/deq/dnre-wb-dwehs-wcu-bestpracticesgeothermal_311868_7.pdf (coolant fluid types)

6Grandstrand, Tyrone, KirtipalBarse, and Jason Schaefer. "Preliminary Analysis of Large-Scale Geothermal Installation at The University of North Dakota." (2011): n. pag. Print.

7www.geokiss.com/software/GHP$-PerfSum9-21-11.xlsx‎ (Price Comparison)

8Daikin Efinity Large Vertical Source Heat Pumps Catalog 1109-5 (Heat Pump Cost)

9http://www.powerknot.com/how-efficient-is-your-air-conditioning-system.html (EER and COP)

10http://www.hdpesupply.com/ (Connectors, etc)

11 http://www.geoproinc.com/ (Bentonite grout cost)

12http://www.chemworld.com/ (Circulating fluid price)

15http://www.npr.org/blogs/money/2011/10/27/141766341/the-price-of-electricity-in-your-state (electricity price)

16 http://www.eia.gov/todayinenergy/detail.cfm?id=10991 (natural gas projection)

10. Appendices

Figure 11.0 Engineering Services Group Design for UT Sorority Village1

Table 10.1 U-Tube Thermal Resistance Information2

Table 10.2 Soil Conductivity2

Table 10.3 Thermal Conductivity of Grouts2

Table 10.1 Geothermal Operational and Maintenance Costs- Optimistic Case

Table 10.2 Geothermal Operational and Maintenance Costs- Nominal Case

Table 10.3 Geothermal Operational and Maintenance Costs-Pessimistic Case

Table 10.4 Conventional HVAC Costs-Optimistic Case

Table 10.5 Conventional HVAC Costs-Nominal Case

Table 10.6 Conventional HVAC Costs- Pessimistic Case

Table 10.7 Conventional HVAC Costs with High Natural Gas Price-Optimistic Case

Table 10.8 Conventional HVAC Costs with High Natural Gas Prices- Nominal Case

Table 10.9 Conventional HVAC Costs with High Natural Gas Prices- Pessimistic Case

Table 10.10 Payback Period-Nominal

Table 10.11 Payback Period- Optimistic

Table 10.12 Payback Period- Pessimistic

Figure 10.2 Grout Volume Calculator11

Figure 10.3 Heat Pump Quote8