Optimal Sensor Placement and Control

of Energy Efficient Buildings

Contents

List of Tables

List of Figures

1 Introduction										      1

1.1	Background and Overview . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 1

1.1.1	Heat Transfer Modeling in Buildings

1.1.2	Model Reduction of Thermodynamic System

1.1.3	LQR Controllers for Energy Efficiency

1.1.4 	SQLC and the SDP

1.2	Literature Review

1.3	Contributions

1.4	Thesis Organization

Abstract— The building sector consumes a large part of the energy used in the United States and is responsible for nearly 40% of greenhouse gas emissions. It is therefore economically and environmentally important to reduce the building energy consumption to realize massive energy savings. Commercial buildings are complex, multi-physics, large scale, and highly stochastic dynamic systems. Recent work has focused on integrating modern modeling, simulation, and control techniques to solving this challenging problem. The overall focus is directed toward designing an optimized and energy efficient building. In this thesis, a method to control room temperature in buildings is proposed. The approach is based on a distributed parameter model represented by a three dimensional (3D) heat equation in a room with heater/cooler located at ceiling. The latter is resolved using finite element methods, and results in a model for room temperature with thousands of states. The latter is not amenable to control design. A reduced order model of only few states is then derived using Proper Orthogonal Decomposition (POD). A Linear Quadratic Regulator (LQR) is computed based on the reduced model, and applied to the full order model to control room temperature.  In this thesis, we employ a constrained stochastic linear quadratic control (SLQC) approach for such purposes. The cost function to be minimized is quadratic, and two different cases are considered. The first case assumes the disturbance is Gaussian and the problem is formulated to minimize the expected cost subject to a linear constraint and a probabilistic constraint. The second case assumes the disturbance is norm-bounded with distribution unknown and the problem is formulated as a min-max problem. By using SLQC, both problems can be reduced to semidefinite optimization problems, where the optimal control may be computed efficiently. Later, some discussions on solving more requirements by SLQC are provided. Simulation results to demonstrate the proposed technique in building model are given.

Keywords: Optimal, Sensor, Placement, LQR, FEM, RHC, Control, Energy, Efficient, Building

Introduction

Background

Buildings are complex multi-scale, multi-physics, and highly uncertain dynamic systems with many sources of disturbances [1].  Whole building simulation presents a formidable computational challenge making the development of design, optimization, and control tools of whole buildings difficult. At a fundamental level, there are several possible approaches to the design and control of high performance buildings. These include: (1) Simulation Based Design, (2) Holistic Fully Integrated Design, and (3) Hybrid Design Methods [1]. Optimal design and control of these systems are very challenging problems and are often done by first developing a reduced order model on which the design is based [1]. This is known as a simulation based design.

Problem Statement

In this thesis, distributed parameter theory is shown to provide useful information about building design and control. We consider the problem illustrated by a single room shown in Figure 1.1.

By solving the system numerically, the dynamical equations of the system with different parameters shed light on the best sensor location, temperature distribution of the room, and the corresponding energy consumption. Finite element theory is used to solve the PDE that describes the cooling and heating process.

The finite element technique is a numerical method for finding approximate solutions of partial differential equations (PDE). The Finite Element Method is a good choice for solving partial differential equations over complicated domains (like cars and oil pipelines), when the domain changes (as during a solid state reaction with a moving boundary), when the desired precision varies over the entire domain, or when the solution lacks smoothness [4],[5],[6].

The approach is based on simplifying the PDE into an approximating system of ordinary differential equations, which are then numerically integrated using standard techniques such as Euler's method, Runge-Kutta, etc. In solving PDEs, the main challenge is to create an equation that approximates the equation to be studied, but is numerically stable, such that errors in the input and intermediate calculations do not accumulate and make the resulting output to be meaningless. The finite element model comprises thousands (18182) states and therefore is not directly amenable to control design. This is due to the fact that the systematic design of optimal controllers based on the full order model results in the former having the same dimension, i.e., thousands of states. This is computational expensive and not feasible in real time. The order of the model needs to be first reduced and then a controller is designed based on the reduced model, and applied to the full order system to control the heat/cooling systems.

Among the multitude of model reduction techniques, the proper orthogonal decomposition (POD) [9] is arguably the most popular method used in deriving reduced models for fluid flows governed by partial differential equations (PDEs) for simulation or control purposes. In POD, snapshots obtained by conducting experiments or computational fluid dynamic (CFD) simulations are usually used to create an ensemble of solutions with particular open loop control input data. The set is used to construct a set of POD basis modes (see e.g. [2]) and a reduced order model is obtained depending on the energy ratio with the full order model [3].

1.2 Literature Review

1.3 Contributions

1.4 Organization

The rest of the paper is organized as follows: In section II we numerically solve the heat transfer problem for the room geometry shown in figure 1.1 using the Finite Elements technique to formulate the full order model of the problem. In section III we control the full order model for the room temperature from section II using the Linear Quadratic Regulator (LQR). In section IV we reduce the model using Proper Orthogonal Decomposition (POD) and then apply the control to the reduced model and compare the results with the full order model control from section III. Finally, section V contains the conclusion and future work.

Thesis Overview

Chapter 2 introduces the existing concepts of proper orthogonal decomposition (POD) and discusses the Finite Element Method of snapshots and the analytical computation of the POD modes for systems described by partial differential equations.

Chapter 3 extends the techniques of Chapter 2 to reduce order model for prototype problems which involve the three-dimensional heat equations. Results from the method of snapshots and solving the modes analytically are compared.

Chapter 4 presents the design methodology for the linear-quadratic regulator controller using the boundary feedback control laws for the resultant finite dimensional system described by the heat equation.

Chapter 5 introduces the concept of constrained stochastic linear quadratic control (SLQC) and show how implementing a Semidefinite Programming approach yields optimal control to this problem.

Chapter 6 briefly summarizes the thesis contributions, and recommendations for future research. Selected references are included at the end of the thesis.

Chapter 1

# Control and Room Temperature Optimization of Energy Efficient Buildings

Add introduction to this section

- Finite Element Solution of the 3d Heat Equation Problem

The cooling and heat flow are modeled by a 3-dimensional (3D) heat equation [7]

|  | (2.1) |
| --- | --- |

where t denotes time,  are spatial coordinated assumed to belong to a domain  which represents the room geometry

is the density in

is the specific heat capacity at constant pressure in

is absolute temperature in

is thermal conductivity in

is the heat source in

The initial temperature is. Boundary condition at the center of the top surface is a fixed temperature at.

The domain of the 3D heat equation  is the room geometry,

- The initial conditions at is

|  | (2.2) |
| --- | --- |

- Dirichlet type boundary condition:

|  | (2.3) |
| --- | --- |

- Neumann type boundary condition

|  | (2.4) |
| --- | --- |

where  is the heat flux, and are Dirichlet and Neumann boundaries respectively as shown in Figure 1.1 where .

The 3D heat equation is multiplied by a basis function  and integrated over the domain  as follows:

|  | (2.5) |
| --- | --- |

The basis function has the following property:

|  | (2.6) |
| --- | --- |

Using the divergence theorem

|  | (2.7) |
| --- | --- |

Using the Neumann boundary condition (2.4) and the basis function property (2.6) we have:

|  | (2.8) |
| --- | --- |

Then the weak formulation of the problem follows

|  | (2.9) |
| --- | --- |

The spatial approximation of solution in the domain   is performed by a linear combination of shape functions, where

| , | (2.10) |
| --- | --- |

whereis the total number of solution nodes and  is the time dependent coefficients. The basis function is also approximated:

|  | (2.11) |
| --- | --- |

Since the basis function is time independent, coefficients will only be numbers. Substitute in the weak form (2.8) and after some derivations; we get the system of ordinary differential equations (ODEs) as follows

|  | (2.12) |
| --- | --- |

where

is the thermal capacity matrix and

is the heat transfer matrix. The system in (2.12) can then be written in state space form as

|  | (2.13) |
| --- | --- |

where ,  and

The plot of one snapshot of the 3D heat diffusion in the room using finite element analysis with the corresponding mesh is shown in Fig 3. One heating/cooling element is assumed to be installed in the room ceiling. Finite element solution at different times is shown in figures 2.3, 2.4, 2.5 and 2.6.

Figure 2.2: The 3D heat equation with corresponding finite element mesh. Number of mesh nodes = number of states = 18182 nodes.

Fig. 2.3: Temperature distribution (in F) after 1 minute

Fig. 2.4: Temperature distribution (in F) after 20 minutes

- Temperature Control

A linear quadratic regulator (LQR) controller [8] is designed to keep the room temperature at the desired value. The control design is based on the reduced order model and applied to the full order system of the form

Fig. 2.5: Temperature distribution (in F) after 40 minutes

Fig. 2.6: Temperature distribution (in F) after 60 minutes.

where is the states vector that contains 18182 temperature values at the nodes shown in the mesh figure. The sensor location is chosen at (04, 0, 0.5), so the measurement equation has the following form:

where   is a vector of zeros everywhere except for the sensor location node where the value is 1. Note that we assumed the temperature is measured by only one sensor.

One of the main issues arising in automatic control of room temperature is the best location of sensors in order to effectively estimate the temperature, especially in the context of using distributed parameter models. From a general point of view, the problem of optimal sensor location can be viewed as the problem of maximizing the output generated by a given state [11], [12]. In room temperature control it is no possible to sense inside the flow domain and full state estimation is not practical. For such problems, the sensors must be located on the boundary, in our case, somewhere on the room walls. In this paper we rely on a search over the domain boundary  for candidate locations to determine the best sensor position. In our simulation the best sensor location is represented in Figure 3.1.

Figure. 3.1: Sensor Location

LQR controller is used as follows: the state-feedback law  minimizes the quadratic cost function:

|  | (3.1) |
| --- | --- |

Subject to the system dynamics

Figure 3.2 shows the step response for two different desired values of 70and 83.

Figure 3.2: Step response for 2 desired set points 70and 83

Note that the closed-loop response is stable and tracks the set points.  The corresponding control input is plotted in the Figure 3.3. A constraint for the input signal to be bounded between 40 F and 150 F is added to account for heating/cooling systems’ saturation.

Chapter 3

- Reduced Order Model Using Pod

With snapshots in hand the correlation matrix  is defined by [10]:

Figure 3.3: Control input

|  | (4.1) |
| --- | --- |

is constructed, where  denoted the usual Euclidean inner product of snapshots .

With denoting the number of POD modes to be constructed, the first eigenvalues of largest magnitude, , of are found. They are sorted in descending order, and their corresponding eigenvectors are calculated. Each eigenvector is normalized so that

|  | (4.2) |
| --- | --- |

.

The orthonormal POD basis set is constructed according to [12]:

|  | (4.3) |
| --- | --- |

where is the component of . With a POD basis in hand, the solution of the distributed parameter model is approximated as a linear combination of POD modes, i.e.,

|  | (4.4) |
| --- | --- |

This shows that POD finds a low dimensional embedding of the snapshots that preserve most of the energy as measured in a much higher dimensional solution space. It is found that taking only the largest 50 eigenvalues keeps 98% of the energy of the full order system. Figures 4.1 and 4.2 show the full order model compared to the reduced order model of 50 modes respectively, both after 40 minutes. Figures 4.3 and 4.4 show the full order model compared to the reduced order model of 50 modes respectively, both after 60 minutes.  It is shown from the figures that the reduced order is so close to the full order which means that working with the reduced order is acceptable and reliable.

Figure 4.1: Full order model at t = 40 minutes

Figure 4.2: Reduced order model at t = 40 minutes

Figure 4.3: Full order model at t = 60 minutes

Figure 4.4: Reduced order model at t = 60 minutes

Step response for both full and reduced controlled system is shown in figure 4.3. The difference lies between 1 or 2 F which is very acceptable considering the large reduction ration from 18182 states to 50. Figure 4.4 shows the input signal for full and reduced order systems. The reduced order controlled input signal leads or lags the full order controlled input signal by 1 or 2 minutes.

- Conclusion

In this paper, we developed a modeling and control approach for room temperature in buildings. The approach is based on a distributed parameter model coupled with high

Figure 4.3: Step response for full and reduced order models

Figure 4.4: Controlled input signal for full order and reduced order controlled systems

performance computing, and modern control theory to regulate room temperature. This theory allows us to study optimal sensor location. The results obtained show excellent performance and are promising for practical implementation. Future research includes coupling the 3D heat equation here with the Boussinesq equation to account for room air flow dynamics. A rigorous study of optimal sensor location is also under investigation.

Chapter 5

# Stochastic Linear Quadratic Control of Energy Efficient Buildings: A Semidefinite Programming Approach

2 Building Climate Plant

In this section, we describe the model used in this work and formulate the problem. The system model was proposed in [4] and employed in [5].

2.1 System Model

The continuous-time dynamics of the room temperature, interior-wall surface temperature, and exterior-wall core temperature, can be represented as follows:

where the parameters in the model above are:

The system states are the room air temperature t1, interior wall surface temperature t2, and exterior wall core temperature t3. The control signals uh and uc represent heating and cooling power, and they can be combined as one variable

u = uh +uc because heating and cooling are not simultaneous. For more details about this model, please refer to [4, 5].

Define the state vector x, the control signal vector u, and the environment stochastic disturbance vector d as:

The state-space model can then be written compactly as:

where

The following constraints are imposed on the temperatures during a day to satisfy the requirement:

Thus, the control constraint can be written in terms of u as:

From above constraints, we can observe that both the room air temperature and control signal are constrained. In the next section, the control problem is formulated.

2.2 Problem Formulation

We consider the problem where the temperature t1 is required to remain within certain bounds of a constant reference tr in the presence of the disturbance vector d. And we can also assign setpoints for both t2 and t3, but without any other constraint on them. Thus, we can regulate the output error e := x−xr, where xr is the setpoint vector of x. Our objective is to find for the system (1) discretized, the M-control sequence {u0; · · · ; uM−1}, where ui := u(ti),i = 0; · · · ; M; ti = iΔT, where △T is the sampling period; and corresponding state sequence {x0; · · · ; xM−1 } and error sequence {e0; · · · ; eM−1}, that minimize the finite horizon objective function:

where E(•) denotes the expectation operator, P ≥ 0; Q ≥ 0 (i.e., semi-definite positive matrices), R > 0 (i.e., positive definite matrix), N is the prediction horizon, M ≤ N is the control horizon, subject to the constraints.

The cost function in this form can be explained as minimizing the temperature errors as well as saving energy. The first problem is formulated with hard constraints (2) and (3).

PROBLEM 1.

subject to (2), (3), and discretized version of (1).

The second problem is formulated with the constraints under the predefined probability to further reduce the energy consumption as temperature confort is a little relaxed. The constraints with probability can be defined as [5]:

where

Gi;gi;Fi; fi are matrices with proper dimensions; and αi;βi ∈[0;1] denote the probability level. Based on this, we can formulate the second problem as:

PROBLEM 2.

subject to (5) and discretized version of (1).

Problem 1 will be addressed with both LQG and RHC methods, while for Problem 2, we will transform it to a convex deterministic second-order cone program (SOCP) and solve it with RHC later.

3 Control Strategies

In this section, we will introduce the control techniques used in this work. We assume that the control center of the building has full state information, i.e., reading from sensors or using a Kalman Filter providing the system is observable.

Then, the control signal will be a function of states.

3.1 Linear Quadratic Gaussian Regulator (LQG)

First, the discretized system can be written as follows:

The LQG controller designed here employs a simple strategy, first compute the LQG control signal which minimizes the cost function, after which the control constraint (3) is applied. That is, if the LQG control signal exceeds the range of the constraint, then it will be cut off from above or below. The discrete-time LQG can be computed as follows [7]:

where

and Pk is calculated iteratively backwards in time by the dynamic Riccati equation:

from initial condition PN = P.

Then, the constrained control input based on LQG is:

where β1;β2 are the lower and upper bound of the control signal.

3.2 Receding Horizon Control (RHC)

The idea of RHC is to start with a fixed optimization horizon, of length N, with the current state as initial state. The steps of RHC are summarised as follows [8]:

• At some time k, with the state xk as initial state, solve the optimal control problem over a fixed length N, from [k;k+N −1], taking the current and future constraints into account.

• Apply the control signal uk corresponding to xk to the system.

• Compute the state obtained at time k+1.

• Repeat the previous three steps from time k+1.

One method to solve the RHC problem is to utilize geometric arguments. The essential idea depends on the nice geometric interpretation in the control-space [8]. The optimal constrained control depends on which partition the state vector lies in. That is, in different partitions, the control is different. Please refer to [8] for more details.

REMARK 1. Note that the different between the RHC used

in this work and the periodic MPC in [6] is that the latter

requires a periodicity of the room temperature, thus only one

day (24 hours) needs to be considered; while in this work,

the RHC applied mainly focuses minimizing the energy cost

(control power) and temperature errors (e).

In order to solve Problem 2 with RHC, we need to further simplify the problem to a tractable problem. For this purpose, assume the disturbance dk follows a Gaussian distribution with mean ¯ dk and variance σ2k

and uk = Fkxk, then by computing iteratively through (8), uk can be written in the linear combination of the disturbances, which coincides the idea in [5] which parameterized the control inputs as affine functions of the disturbance sequence.

Thus, control inputs can be written as [5]:

In the matrix form it leads to

u = Md+h

Also define . And write the prediction dynamics in the form: x = Ax0+Bu+Dd Thus, follow [5], the constraints with probability can be equivalently formulated as deterministic second order cone constraints. Moreover,

Problem 2 can be reformulated as a SOCP:

subject to

where Φ is the Gaussian cumulative probability corresponding to di.

REMARK 2. Note that the cost function considered in this thesis is quadratic function in contrast to the one used in [5] which is a linear function of u. Moreover, the objective here includes not only minimizing the control power, but also reducing the error between room temperature and the default value.

REMARK 3. The SOCP problem is a nonlinear convex optimization problem. There are several algorithms that can provide a solution, i.e., Interior point method [9].

4 Simulation Results

In this section, simulation results are given to illustrate the proposed methods. The parameters of the climate model are given in section 2. The continuous-time system (1) is sampled with a zero-order hold and a sample-period of 10min, resulting 144 samples per day. The initial temperatures are set to be [72:5◦F;69:8◦F;64:4◦F]. The temperature reference trajectory is xr = [74:3◦F;74:3◦F;68:0◦F].

The cost matrices Q;R are chosen: Q = diag(1;0;0) and R = 0:00002. Note that the smaller the R is, the faster the response will be but with more cost on inputs. The disturbance d in one day (assume it is periodic with period 24 hours) in this example is plotted:

4.1 LQG Performance

First, we apply the constrained LQR controller (12). The temperature t1 and control power in 10 days are plotted in Fig. 2. It is obvious that t1 fluctuates around the set point temperature and in the range of constraint. However, some control inputs exceeds the range of the requirement and thus cut off at the boundaries.

We perform one more simulation in Fig. 3 which removes the constraint on the control power for comparison. We can observe without the control constraints, t1 fluctuates around the set point with a smaller fluctuation magnitude compared with Fig. 2, but the price is more power cost.

4.2 RHC Performance

The RHC controller can be written in the linear form:

where the superindex r denotes the active region, i.e. the region which contains the given state xk. To calculate the solution, we employ the Multi-Parametric Toolbox [10]. We increase R = 0:001, and compute the optimal solution to the finite horizon control problem with N = 5. The solution consists of 51 regions, and the result is plotted in Fig. 4 which shows that the room temperature stays within the required range with less energy consumption than the preceding control.

4.3 Stochastic RHC for Problem 2

Next, we focus on Problem 2. The probability levels for the temperature and control power are chosen as: αi = 0:2 and βi = 0:2. The disturbances to the system are the same as in Fig. 1, while approximately considered as Gaussian.

The optimization problem is solved by interior point method and then applied RHC with finite horizon N = 2 and R = 0:00002. t1 and u are plotted in Fig. 5 which shows that the room temperature is within the desired range with additional energy savings.

5 Conclusion

In this work, we focused on constrained quadratic control of room temperature on a building climate dynamical model.

Constrained LQR and RHC are employed to solve stochastic optimization problems, and stochastic RHC is used to solve the problem with chance constraints. Future work will focus on robust control strategy with chance constraints.

Conclusion

References

- J. Borggaard, J. A. Burns, A. Surana, and L. Zietsman, Control, Estimation and Optimization of Energy Efficient Buildings, Proceedings of the American Control Conference, St. Louis, MO, USA June 10-12, 2009, pp. 837-841.

- R.C. Camphouse,  “Boundary Feedback Control Using Proper Orthogonal Decomposition Models,” Journal of Guidance, Control, and Dynamics, Vol. 28, No. 5, September-October 2005, pp. 931-938.

- S. Sahyoun and S.M. Djouadi, Nonlinear Model Reduction for Fluid Flows, Proceedings of the American Control Conference, San Francisco, June 28-July 1, 2011.

- E. Stein (2009), Olgierd C. Zienkiewicz, a pioneer in the development of the finite element method in engineering science. Steel Construction, 2 (4), 264-272.

- Strang, Gilbert; Fix, George (1973). An Analysis of The Finite Element Method. Prentice Hall. ISBN 0130329460.

- P. Solin, K. Segeth, I. Dolezel: Higher-Order Finite Element Methods, Chapman & Hall/CRC Press, 2003

- Crank, J.; Nicolson, P.; Hartree, D. R. (1947), "A Practical Method for Numerical Evaluation of Solutions of Partial Differential Equations of the Heat-Conduction Type", Proceedings of the Cambridge Philosophical Society 43: 50–67.

- Kwakernaak, Huibert and Sivan, Raphael (1972). Linear Optimal Control Systems. First Edition. Wiley-Interscience. ISBN 0-471-511102.

- Holmes, P., Lumley, J. L., & Berkooz, G. (1996). Turbulence, coherent structures, dynamical systems and symmetry. Cambridge: Cambridge University Press.

- R.C. Camphouse,  “Boundary Feedback Control Using Proper Orthogonal Decomposition Models,” Journal of Guidance, Control, and Dynamics, Vol. 28, No. 5, September-October 2005, pp. 931-938.

- D. Georges, The Use of Observability and Controllability Gramians or Functions for Optimal Sensor and Actuator Location in Finite-Dimensional Systems, Proceedings of the 34th Conference on Decision & Control New Orleans, LA - December 1995, pp. 3319-3324.

- J.A. Burn and B.B. King, Optimal sensor location for robust control of distributed parameter systems, Proceedings of the 33rd Conference on Decision and Control Lake Buena Vista, FL - December 1994, pp. 3967-3972.

- comsol.com

- [1] J.M. McQuade. ”A system approach to high performance buildings,” Technical report, United Technologies Corporation, February 2009.

- http://gop.science.house.gov/Media/hearings/energy09/april28/

- mcquade.pdf.

- [2] Y. Ma, F. Borrelli, B. Hencey, A. Packard, and S. Bortoff, ”Model Predictive Control of Thermal Energy Storage in

- Building Cooling Systems,” Proceedings of the Joint 48th Conference on Decision and Control and 28th Chinese Control Conference, Shanghai, P.R. China, December 16-18, 2009, pp. 392-397.

- [3] J. Borggaard, J. A. Burns, A. Surana, and L. Zietsman, ”Control, Estimation and Optimization of Energy Efficient Buildings,” Proccedings of the American Control Conference, St. Louis, MO, USA June 10-12, 2009, pp. 837-841.

- [4] M. Gwerder and J. Todtli, ”Predictive Control for Integrated Room Automation,” 8th REHVA World Congress for Building Technologies-CLIMA, Switzerland, 2005.

- [5] F. Oldewurtel, A. Parisio, C.N. Jones, M. Morari, D. Gyalistras, M. Gwerder, V. Stauch, B. Lehmann, and K. Wirth,

- ”Energy Efficient Building Climate Control using Stochastic Model Predictive Control andWeather Predictions,” Proceedings of the American Control Conference, Baltimore, MD, USA June 30-July 02, 2010, pp. 5100-5105.

- [6] R. Gondhalekar, F. Oldewurtel, and C.N. Jones, ”Least-Restrictive Robust MPC of Periodic Affine Systems with Application to Building Climate Control,” Proceeings of the 49th IEEE Conference on Decision and Control, pp. 5257-5263, December 15-17, 2010.

- [7] H. Kwakernaak, and R. Sivan, Linear Optimal Control Systems. First Edition. Wiley-Interscience, 1972.

- [8] G.G. Goodwin, M.M. Seron, and J.A. De Dona, Constrained Control and Estimation: An Optimization Approach,

- Springer, 2005.

- [9] Margaret H. Wright, ”The interior-point revolution in optimization: history, recent developments, and lasting consequences”. Bull. Amer. Math. Soc. (N.S), vol 42, pp. 39C56,

- 2005.

- [10] M. Kvasnica, P. Grieder, and M. Baotic, Multi-Parametric Toolbox (MPT), http://control.ee.ethz.ch/ mpt/, 2004.

- [11] M. Koschenz and B. Lehmann. ”Development of a thermally activated ceiling panel with pcm for application in lightweight and retrofitted buildings,” Energy and Buildings, vol. 36(6), pp. 567 - 578, 2004.